## Sheet1
PARAMETERS | UoM | DESIGN | OPERATING
BASIC INPUTS
LOAD | MW | 300 | 299.5
AMBIENT PRESSURE | bar(a) | 1.013 | 1.013
AMBIENT TEMPERATURE | °C | 27.5 | 27.5
RELATIVE HUMIDITY | % | 60 | 60
COAL ANALYSYS
PROXIMATE ANALYSIS OF COAL( AFB)
MOISTURE CONTENT IN COAL | % | 11 | 11
ASH CONTENT IN COAL | % | 11.12 | 11.12
FIXED CARBON IN COAL | % | 46.22 | 46.22
VOLATILE MATTER IN COAL | % | 31.66 | 31.66
ULTIMATE ANALYSIS OF COAL( AFB)
MOISTURE CONTENT IN COAL | % | 11 | 11
ASH CONTENT IN COAL | % | 11.12 | 11.12
TOTAL CARBON IN COAL | % | 64.6 | 64.6
HYDROGEN CONTENT IN COAL | % | 4.75 | 4.75
NITROGEN CONTENT IN COAL | % | 2.24 | 2.24
SULPHER CONTENT IN COAL | % | 0.3 | 0.3
OXYGEN CONTENT IN COAL | % | 5.99 | 5.99
SUM | % | 100 | 100
GCV OF COAL | kCal/kg | 6300 | 6300
LOSS OF IGNITION
UNBURNT CARBON IN FLY ASH | % | 3.4 | 3.4
UNBURNT CARBON IN BOTTOM ASH | % | 3.4 | 3.4
% of Flyash to Total Ash | % | 90 | 90
% of Bottom ash to Total Ash | % | 10 | 10
MS PRESSURE AT BOILER O/L | MPa (a) | 16.89 | 11.94
MS FLOW | TPH | 906.2 | 906.2
TOTAL FEED WATER FLOW | TPH | 971.09 | 971.09
DESUPERHEATING
RH LHS DESUP FLOW | TPH | 0 | 0
RH RHS DESUP FLOW | TPH | 2.99 | 2.99
1ST STAGE SHS DESUP FLOW | TPH | 1.76 | 1.76
2ND STAGE SHS DESUP FLOW | TPH | 0 | 0
SH SPRAY WATER PRESSURE | MPa (a) | 18.77 | 18.77
SH SPRAY WATER TEMP | °C | 169.99 | 169.99
RH SPRAY WATER PRESSURE | MPa (a) | 11.8 | 11.8
RH SPRAY WATER TEMP | °C | 160.9 | 160.9
PULVERISER
MILL-A CURRENT | Amps | 29.22 | 29.22
MILL-B CURRENT | Amps | 30.18 | 30.18
MILL-C CURRENT | Amps | -0.04 | -0.04
MILL-D CURRENT | Amps | 32.93 | 32.93
MILL-E CURRENT | Amps | 32.33 | 32.33
MILL-F CURRENT | Amps | -0.1 | -0.1
MILL- A COAL FLOW | TPH | 25.14 | 25.14
MILL- B COAL FLOW | TPH | 24.9 | 24.9
MILL- C COAL FLOW | TPH | 0.74 | 0.74
MILL- D COAL FLOW | TPH | 30.95 | 30.95
MILL- E COAL FLOW | TPH | 31.24 | 31.24
MILL- F COAL FLOW | TPH | 0.1 | 0.1
TOTAL COAL FLOW | TPH | 112.3 | 112.3
MILL-A O/L TEMP | °C | 80.02 | 80.02
MILL-B O/L TEMP | °C | 76.11 | 76.11
MILL-C O/L TEMP | °C | 47.83 | 47.83
MILL-D O/L TEMP | °C | 74.88 | 74.88
MILL-E O/L TEMP | °C | 73.05 | 73.05
MILL-F O/L TEMP | °C | 48.5 | 48.5
APH
APH-A I/L FLUE GAS TEMP-1 | °C | 340.05 | 340.05
APH-A I/L FLUE GAS TEMP-2 | °C | 337 | 337
APH-A O/L FLUE GAS TEMP-1 | °C | 133.95 | 133.95
APH-A FLUE GAS O/L TEMP-2 | °C | 143.95 | 143.95
APH-B I/L FLUE GAS TEMP-1 | °C | 339.4 | 339.4
APH-B I/L FLUE GAS TEMP-2 | °C | 340 | 340
APH-B O/L FLUE GAS TEMP-1 | °C | 139.14 | 139.14
APH-B FLUE GAS O/L TEMP-2 | °C | 144.66 | 144.66
APH-A PA I/L TEMP | °C | 39.76 | 39.76
APH-B PA I/L TEMP | °C | 39.44 | 39.44
APH -A OUT PRI AIR TEMP | °C | 288.02 | 288.02
APH -B OUT PRI AIR TEMP | °C | 287.82 | 287.82
APH -A SEC. AIR IN TEMP | °C | 33.78 | 33.78
APH -B SEC. AIR IN TEMP | °C | 33.3 | 33.3
APH -A SEC AIR OUTLET TEMP | °C | 295.49 | 295.49
APH -B SEC AIR OUTLET TEMP | °C | 295.96 | 295.96
APH -A INLET P.A PRESSURE | kPa (a) | 8.29 | 8.29
APH -B INLET P.A PRESSURE | kPa (a) | 8.19 | 8.19
PA HEADER PRESSURE APH-A O/L | kPa (a) | 7.61 | 7.61
PA HEADER PRESSURE APH-B O/L | kPa (a) | 7.97 | 7.97
APH -A INLET S.A PRESSURE | kPa (a) | 1.6 | 1.6
APH -B INLET S.A PRESSURE | kPa (a) | 1.62 | 1.62
APH -A OUTLET S.A PRESSURE | kPa (a) | 0.66 | 0.66
APH -B OUTLET S.A PRESSURE | kPa (a) | 0.77 | 0.77
APH-A INLET FLUE GAS PRESSURE | kPa (a) | -1.07 | -1.07
APH-B INLET FLUE GAS PRESSURE | kPa (a) | -1.03 | -1.03
APH-A OUTLET FLUE GAS PRESSURE | kPa (a) | -1.96 | -1.96
APH-B OUTLET FLUE GAS PRESSURE | kPa (a) | -1.95 | -1.95
APH-A I/L FLUE GAS OXYGEN CONTENT | % | 5.06 | 5.06
APH-A O/L FLUE GAS OXYGEN CONTENT | % | 5.13 | 5.13
APH-B I/L FLUE GAS OXYGEN CONTENT | % | 5.15 | 5.15
APH-B O/L FLUE GAS OXYGEN CONTENT | % | 5.71 | 5.71
TOTAL SEC AIR FLOW | TPH | 790 | 790
TOTAL PRIMARY AIR FLOW | TPH | 220.01 | 220.01
BURNER TILT POSITION | % | 73.99 | 73.99
FURNACE DRAFT SET POINT | % | -0.12 | -0.12
PA HEADER PRESSURE SET POINT | kPa (a) | 7.6 | 7.6
FANS: ID, FD & PA
FD FAN A CURRENT | Amps | 35.42 | 35.42
FD FAN B CURRENT | Amps | 34.97 | 34.97
FDF-A BLADE PITCH | % | 35.52 | 35.52
FDF-B BLADE PITCH | % | 39.15 | 39.15
FDF-A I/L SA TEMP | °C | 29.04 | 29.04
FDF-B I/L SA TEMP | °C | 29.98 | 29.98
FDF-A DISCHARGE PRESS | kPa (a) | 1.52 | 1.52
FDF-B DISCHARGE PRESS | kPa (a) | 1.53 | 1.53
ID Fan A Current | Amps | 90.29 | 90.29
ID Fan B Current | Amps | 92.55 | 92.55
IDF-A I/L PRESS | kPa (a) | -2.28 | -2.28
IDF-B I/L PRESS | kPa (a) | -2.4 | -2.4
IDF-A I/L TEMP | °C | 131.67 | 131.67
IDF-B I/L TEMP | °C | 132.26 | 132.26
IDF-A SCOOP POSITION | % | -2.41 B | -2.41 B
IDF-B SCOOP POSITION | % | 0.45 B | 0.45 B
IDF-A SPEED | RPM | 551.94 | 551.94
IDF-B SPEED | RPM | 551.23 | 551.23
IDF-A DISCHARGE PRESS | kPa (a) | -0.03 | -0.03
IDF-B DISCHARGE PRESS | kPa (a) | 0.01 | 0.01
PAF-A CURRENT | Amps | 79.46 | 79.46
PAF-B CURRENT | Amps | 66.92 | 66.92
PAF-A SCOOP POSITION | % | 48.2 | 48.2
PAF-B SCOOP POSITION | % | 40.97 | 40.97
PAF-A SPEED | RPM | 1102 | 1102
PAF-B SPEED | RPM | 1022.14 | 1022.14
PAF-A DISCHARGE PRESS | kPa (a) | 8.55 | 8.55
PAF-B DISCHARGE PRESS | kPa (a) | 8.32 | 8.32
ID FAN-A VFD CURRENT | Amps | 138.12 | 138.12
ID FAN-B VFD CURRENT | Amps | 141.75 | 141.75
CEMS
FG TEMP AT CHIMNEY |  | 3.49 B | 3.49 B
CHIMNEY NOX |  | 328.98 | 328.98
CHIMNEY SOX |  | 530.58 | 530.58
CHIMNEY SPM |  | -1.16 B | -1.16 B
Radiation & Unaccounted Loss | % | 0.94 | 0.94